DISCONTINUED PRODUCT

Liebert® Challenger ITR™

GUIDE SPECIFICATIONS
Nominal 23 or 33 kW
Environmental Control System

# GENERAL

## SUMMARY

These specifications describe requirements for an environmental control system. The system shall be designed to maintain temperature and relative humidity conditions within the room. The manufacturer shall design and furnish all equipment to be fully compatible with heat dissipation requirements of the site.

## Design Requirements

The environmental control system shall be a Liebert Challenger ITR factory-assembled unit. Standard 60 Hz units shall be CSA (NRTL-C) certified. It shall be specifically designed for service from the front and rear of the unit. The system shall be designed for draw-through air arrangement to insure even air distribution to the entire face area of the coil.

Each system shall be capable of handling ____ CFM (CMH) at ____inches (mm) of water external static pressure with a horizontal airflow pattern. It shall have a total cooling capacity of ____ BTU/HR (kW), sensible cooling capacity of ____ BTU/HR (kW), based on the entering air condition of °F (°C) dry bulb, and ____ °F (°C) wet bulb. These units are to be supplied with ____ Volt, ____ phase, ____ Hz power supply. The humidifier shall have a capacity of ____ lbs/hr (kg/h). Reheat shall have a capacity of _____ BTU/HR (kW). The main fan shall be ____ hp (kW).

## Submittals

Submittals shall be provided with the proposal and shall include: Single-Line Diagrams; Dimensional, Electrical, and Capacity data; Piping and Electrical Connection Drawings.

# Product

## All Systems

### Cabinet and Frame Construction

The frame shall be constructed of MIG welded tubular and formed steel. All frame components shall be finished in a black, powder-coat finish to protect against corrosion. The exterior panels shall be 20 gauge steel and shall be powder coated with ____ color paint. The panels shall be insulated with a minimum 1 in. (25.4mm), 1-1/2 lbs. (0.68 kg) density fiber insulation. Front and side panels shall have captive, 1/4 turn fasteners.

The cabinet shall be designed so that all components are serviceable and removable from the front and rear of the unit.

### Fan and Motor Section

The fan shall be the centrifugal type, double width, double inlet. The shaft shall be heavy duty steel with self-aligning ball bearings with minimum life span of 100,000 hours.

The fan motor shall be 1750 RPM and mounted on an adjustable base. The drive package shall be sized for 200% of the fan motor horsepower, and equipped with an adjustable motor pulley. The fan/motor assembly shall be mounted on (vibration isolators) (solid base). The fan shall be located to draw air over the coil to ensure even air distribution and maximum coil performance.

High Efficiency Motor (Optional)

The fan motor shall be a ____ hp (kW) high efficiency motor with a full load efficiency of ____ %.

### Filter

The filter shall be____ inches (mm) thick and rated not less than _____ % (20%, 30%, 40-45%, 60-65%) efficiency based on ASHRAE 52.1.

Prefilter (Optional)

The prefilter shall be 2 in. (50.8mm) thick with an efficiency of 20% based on ASHRAE 52.1.

### Advanced Microprocessor Control (Standard)

The Advanced control processor shall be microprocessor based with a front monitor LCD display panel and control keys for user inputs. The controls shall be menu driven with on-screen prompts for easy user operation. The system shall allow user review and programming of temperature and humidity setpoints, alarm parameters, and setup selections including choice of control type. A password shall be required to make system changes. For all user selections, the range of acceptable input (temperature, humidity, or time delay) shall be displayed on the monitor screen. The system shall provide monitoring of room conditions, operational status in % of each function, component run times, date and time, and four analog inputs from sensors provided by others.

Control

The control system shall allow programming of the following room conditions:

- Temperature Setpoint 65 to 85°F (18-29°C)

- Temperature Sensitivity +1 to +9.9°F (0.6 to 5.6°C) in 0.1° increments

- Humidity Setpoint 20 to 80% RH

- Humidity Sensitivity +1 to +30% RH

All setpoints shall be adjustable from the individual unit front monitor panel. The microprocessor can be set within these ranges, however, the unit may not be able to control to extreme combinations of temperature and humidity.

Temperature and Humidity Sensors shall be capable of being calibrated using the front monitor panel controls to coordinate with other temperature and humidity sensors in the room.

Predictive Humidity Control

The microprocessor shall calculate the moisture content in the room and prevent unnecessary humidification and dehumidification cycles by responding to changes in dew point temperature.

Compressor Short-Cycle Control

The control system shall include a program to prevent compressor short-cycling.

System Auto-Restart

For start-up after power failure, the system shall provide automatic restart with a programmable (up to 9.9 minutes in 6-second increments) time delay. Programming can be performed either at the unit or from the central site monitoring system.

Sequential Load Activation

During start-up, or after power failure, the microprocessor shall sequence operational load activation to minimize inrush current. Systems allowing multiple loads to start simultaneously are unacceptable.

Chilled Water/Hot Water/Econ-O-Coil Flush Cycles

Chilled water, hot water, and Econ-O-Cool coils (if unit is so equipped) shall be automatically flushed to prevent the buildup of contaminants. Systems without this feature shall include the necessary devices to bypass fluid into the coil on a programmed basis.

Front Monitor Display Panel

The microprocessor shall provide a front monitor LCD backlit display panel with 4 rows of 20 characters with adjustable contrast. This display (along with five front mounted control keys) shall be the only operator interface required to obtain all available system information such as room conditions, operational status, alarms, control and alarm setpoints, and all user selections including alarm delays, sensor calibration, DIP switch selections, and diagnostics. All indicators shall be in language form. No symbols or codes shall be acceptable.

Alarms

The microprocessor shall activate an audible and visual alarm in event of any of the following conditions:

- High Temperature

- Low Temperature

- High Humidity

- Low Humidity

- Short Cycle

- Compressor Overload (Optional)

- Main Fan Overload (Optional)

- Humidifier Problem

- High Head Pressure

- Change Filter

- Loss of Air Flow

- Low Suction Pressure

- Loss of Power

- Custom Alarm (#1 to #4)

Custom alarms are four customer accessible alarm inputs to be indicated on the front panel. Custom alarms can be identified with prepared (programmed) alarm labels for the following frequently used inputs:

- Water Under Floor

- Smoke Detected

- Standby GC Pump On

- Loss of Water Flow

- Standby Unit On

User customized text can be entered for two of the four custom alarms. Each alarm (unit and custom) can be separately enabled or disabled, selected to activate the common alarm, and programmed for a time delay of 0 to 255 seconds.

Audible Alarm

The audible alarm shall annunciate any alarm that is enabled by the operator.

Common Alarm

A programmable common alarm shall be provided to interface user selected alarms with a remote alarm device.

Remote Monitoring

All alarms shall be communicated to the Liebert monitoring system with the following information: date and time of occurrence, unit number, and present temperature and humidity.

Analog Inputs

The system shall include four customer accessible analog inputs for sensors provided by others. The analog inputs shall accept a 4 to 20 mA signal. The user shall be able to change the input to 0 to 5 VDC or 0 to 10 VDC if desired. The gains for each analog input shall be programmable from the front panel. The analog inputs shall be able to be monitored from the front panel.

Diagnostics

The control system and electronic circuitry shall be provided with self-diagnostics to aid in troubleshooting. The microcontroller board shall be diagnosed and reported as pass/not pass. Control inputs shall be indicated as on or off at the front monitor panel. Control outputs shall be able to be turned on or off from the front monitor panel without using jumpers or a service terminal. Each control output shall be indicated by an LED on a circuit board.

Data Collection

The control system shall maintain accumulative operating hours of compressor, reheat, humidifier, fan motor, and Econ-O-Coil. The ten most recent alarms shall also be retained.

Communications

The microprocessor shall be compatible with all Liebert remote monitoring and control devices.

### Advanced Microprocessor Control with Graphics (Optional)

The optional Advanced control processor shall be microprocessor based with a front monitor dot matrix display panel and control keys for user inputs. The controls shall be menu driven with on-screen prompts for easy user operation. The system shall allow user review and programming of temperature and humidity setpoints, alarm parameters, and setup selections including choice of control type. A password shall be required to make system changes. For all user selections, the range of acceptable input (temperature, humidity, or time delay) shall be displayed on the monitor screen. The system shall provide monitoring of room conditions, operational status in % of each function, component run times, date and time, and four analog inputs from sensors provided by others.

Control

The control system shall allow programming of the following room conditions:

- Temperature Setpoint 65 to 85°F (18-29°C)

- Temperature Sensitivity +1 to +9.9°F (0.6 to 5.6°C) in 0.1° increments

- Humidity Setpoint 20 to 80% RH

- Humidity Sensitivity +1 to +30% RH

All setpoints shall be adjustable from the individual unit front monitor panel.

Temperature and Humidity Sensors shall be capable of being calibrated using the front monitor panel controls to coordinate with other temperature and humidity sensors in the room.

Predictive Humidity Control

The microprocessor shall calculate the moisture content in the room and prevent unnecessary humidification and dehumidification cycles by responding to changes in dew point temperature.

Compressor Short-Cycle Control

The control system shall include a program to prevent compressor short-cycling.

System Auto-Restart

For start-up after power failure, the system shall provide automatic restart with a programmable (up to 9.9 minutes in 6-second increments) time delay. Programming can be performed either at the unit or from the central site monitoring system.

Sequential Load Activation

During start-up, or after power failure, the microprocessor shall sequence operational load activation to minimize inrush current. Systems allowing multiple loads to start simultaneously are unacceptable.

Chilled Water/Hot Water/Econ-O-Coil Flush Cycles

Chilled water, hot water, and Econ-O-Cool coils shall be automatically flushed to prevent the buildup of contaminants. Systems without this feature shall include the necessary devices to bypass fluid into the coil on a programmed basis.

Front Monitor Display Panel

The microprocessor shall provide a front monitor 240 x 120 dot matrix display panel with adjustable backlighting. This display (along with five front mounted control keys) shall be the only operator interface required to obtain all available system information such as room conditions, operational status, graphical data, alarms, control and alarm setpoints, and all user selections including alarm delays, sensor calibration, DIP switch selections, and diagnostics. All indicators shall be in language form. No symbols or codes shall be acceptable.

Alarms

The microprocessor shall activate an audible and visual alarm in event of any of the following conditions:

- High Temperature

- Low Temperature

- High Humidity

- Low Humidity

- Short Cycle

- Compressor Overload (Optional)

- Main Fan Overload (Optional)

- Humidifier Problem

- High Head Pressure

- Change Filter

- Loss of Air Flow

- Low Suction Pressure

- Loss of Power

- Custom Alarm (#1 to #4)

Custom alarms are four customer accessible alarm inputs to be indicated on the front panel. Custom alarms can be identified with prepared (programmed) alarm labels for the following frequently used inputs:

- Water Under Floor

- Smoke Detected

- Standby GC Pump On

- Loss of Water Flow

- Standby Unit On

User-customized text can be entered for all four custom alarms. Each alarm (unit and custom) can be separately enabled or disabled, selected to activate the common alarm, and programmed for a time delay of 0 to 255 seconds.

Audible Alarm

The audible alarm shall annunciate any alarm that is enabled by the operator.

Common Alarm

A programmable common alarm shall be provided to interface user selected alarms with a remote alarm device.

Remote Monitoring

All alarms shall be communicated to the Liebert site monitoring system with the following information: date and time of occurrence, unit number, and present temperature and humidity.

Analog Inputs

The system shall include four customer accessible analog inputs for sensors provided by others. The analog inputs shall accept a 4 to 20 mA signal. The user shall be able to change the input to 0 to 5 VDC or 0 to 10 VDC if desired. The gains for each analog input shall be programmable from the front panel. The analog inputs shall be able to be monitored from the front panel.

Diagnostics

The control system and electronic circuitry shall be provided with self-diagnostics to aid in troubleshooting. The microcontroller board shall be diagnosed and reported as pass/not pass. Control inputs shall be indicated as on or off at the front monitor panel.

Control outputs shall be able to be turned on or off from the front monitor panel without using jumpers or a service terminal. Each control output shall be indicated by an LED on a circuit board.

Data Collection

The control system shall maintain accumulative operating hours of compressor, reheat, humidifier, fan motor, Econ-O-Coil, and heat rejection. The sixty most recent alarms shall also be retained.

Graphing

The control shall display the following graphical data:

- Temperature, humidity, analog inputs

- Component operating status by hour

- Operating status

Communications

The microprocessor shall be compatible with all Liebert remote monitoring and control devices.

### Infrared Humidifier (Standard)

The humidifier shall be of the infrared type consisting of high intensity quartz lamps mounted above and out of the water supply. The evaporator pan shall be stainless steel and arranged to be serviceable without disconnecting water supply lines, drain lines or electrical connections. The complete humidifier section shall be pre-piped ready for final connection. The infrared humidification system shall use bypass air to prevent over-humidification of the controlled space. The auto flush system shall automatically flush deposits from the humidifier pan. The system shall be field adjustable to change the cycle time to suit local water conditions. The humidifier shall have a capacity of _____ lbs/hr (kg/h).

### Steam Generating Humidifier (Optional)

The environmental control system shall be equipped with a steam generating humidifier that is controlled by the microprocessor control system. It shall be complete with disposable canister, all supply and drain valves, steam distributor, and electronic controls. The need to change canister shall be annunciated on the microprocessor control panel. The humidifier shall have a capacity of ____ lbs/hr (kg/h).

### Electric Reheat (Standard)

The low-watt density, 304/304, stainless steel, finned-tubular electric reheat coils shall be capable of maintaining room dry bulb conditions when the system is calling for dehumidification. The reheat section shall include UL recognized safety switches to protect the system from overheating. The capacity of the reheat coils shall be ____ BTU/HR (kW), ____ kW, controlled in ____ stage(s).

### Hot Water Reheat (Optional)

The hot water reheat coil shall have copper tubes and aluminum fins with a capacity of _____ BTU/HR (kW) when supplied with _____ °F (°C) entering water temperature at _____GPM (l/s) flow rate. Maximum pressure drop shall be _____ PSI (kPa). The control system shall be factory pre-piped with a 2-way motorized control valve and cleanable Y-strainer.

### SCR Electric Reheat (Optional)

The SCR (Silicon Controlled Rectifier) controller shall proportionally control the stainless steel reheats to maintain the selected room temperature. The rapid cycling made possible by the SCR controller provides precise temperature control, and the more constant element temperature improves heater life. The capacity of the reheat coils shall be _____ BTU/HR (kW).

### Floor Stand (Optional)

The floor stand shall be constructed of a heliarc-welded tubular steel frame. The floor stand shall be coated using an autodeposition process to protect against corrosion. The floor stand shall have adjustable legs with vibration isolation pads. The floor stand shall be: 9 in. (23cm), 12 in. (30cm), 15 in. (38cm), 18 in. (46cm), 21 in. (53cm), 24 in. (61cm) high.

### Plenum

The unit shall be supplied with a (2 way) (3 way) (4 way) (low-profile, cold-aisle) air discharge plenum. The plenum shall be 18 in. (457mm) high or less, insulated and powder painted the same color as the room unit.

### Disconnect Switch, Locking Type

The manual disconnect switch shall be mounted in the high voltage section of the electrical panel. The switch shall prevent access to the high voltage electrical components until switched to the “OFF” position.

### Remote Sensors (Required for Select Applications)

The unit shall be supplied with remote temperature and humidity sensors. The sensors shall be connected to the unit by a 30 ft. (9m), 60 ft. (18m), 90 ft. (27m), 120 ft. (36m), 150 ft. (45m) shielded cable.

### Remote Sensor Installation Location

The remote temperature and humidity sensor should be installed in the cold aisle in front of the equipment to be cooled. It should be mounted at the farthest point from the cooling unit that supply air needs to reach but still within the unit’s area of influence. The sensor should be installed at the highest point that equipment will draw in cooled air.

### Firestat (Optional)

The firestat shall immediately shut down the system when high temperatures are detected. The firestat shall be mounted in the electrical panel with the sensing element in the return air.

### Smoke Detector (Optional)

The smoke detector senses the return air, shuts down the unit upon detection, and sends visual and audible alarm. Dry contacts are available for a remote customer alarm. This smoke detector is not intended to function as or replace any room smoke detection system that may be required by local or national codes.

### Condensate Pump

The condensate pump shall have the capacity of ____ GPH (l/h) at ____ ft. (m) head @ ____ V - ____ Hz. It shall be complete with (single) (dual) integral float switch, pump, motor assembly, and reservoir.

## Direct Expansion Self-Contained Systems

Direct Expansion Coil

The evaporator coil shall have _____ sq.ft. (sq. m) face area, _____ rows deep. It shall be configured as V-frame and be constructed of copper tubes and aluminum fins and have a maximum face velocity of _____ ft. per minute (m/s) at _____ CFM (CMH). The coil shall be provided with a stainless steel drain pan.

Refrigeration System

The refrigeration system shall consist of a high efficiency scroll compressor, hot gas bypass, pressure safety switches, externally equalized expansion valve, filter drier, refrigerant sight glass and moisture indicator.

### Air-Cooled Self-Contained Systems

Pump Down Control

A liquid line solenoid valve shall be provided for pump down control.

Crankcase Heater

A crankcase heater shall be provided for additional system protection from refrigerant migration during off cycles.

Propeller Fan Condenser (Standard)

The Liebert manufactured air-cooled condenser shall be the low profile, slow speed, direct-drive, propeller-fan type. The condenser shall be constructed of aluminum and contain a copper tube, aluminum fin coil with an integral electric control panel. The system shall be designed for _____ °F (°C) ambient. The air-cooled condenser shall have a _____ Volt, _____ phase, ____ Hz power supply.

Fan Speed Control (FSC) Head Pressure Control (Standard)

The winter control system for the air-cooled condenser shall be Liebert Fan Speed Control (FSC). The variable speed motor shall turn on at 10% of the supply voltage and modulate in response to head pressure to a full speed of 1050 RPM. It shall be designed with ball bearings, permanent lubrication, and internal overload protection.

The control system shall be complete with transducers, thermostats and electrical control circuit, factory prewired and tested in an integral control panel. The transducer shall automatically sense the head pressure of the compressor and control the variable speed fan on the air-cooled condenser to properly maintain the head pressure.

The fan speed control system shall provide positive start-up and operation in ambient temperature as low as -20°F (-29°C). Included with the fan speed control system shall be a solid state winter start kit as an integral feature of the electronic control panel.

Liebert Lee-Temp Head Pressure Control (Optional)

The winter control system for the air-cooled condenser shall be “Liebert Lee-Temp.” The Liebert Lee-Temp system shall allow startup and positive head pressure control with ambient temperatures as low as -30°F (-34.4°C). The Liebert Lee-Temp package shall include: insulated receiver, pressure relief valve for each circuit, head pressure three-way control valve, and rotalock valve for isolating the refrigerant charge. The Lee- Temp receiver shall be factory insulated and mounted ready for the field connection to the air-cooled condenser. The Liebert Lee-Temp heater shall be (150) (300) _____ Watt and require a separate power supply of (115) (230) _____ Volt, single phase, _____ Hz.

Centrifugal Fan Condenser (Optional)

The system shall be supplied with a centrifugal fan condenser (LCC). The condenser shall be constructed of galvanized steel with a copper tube, aluminum fin coil. The heavy duty fan shall be the centrifugal type, double width, double inlet. The 1750 RPM (1450 RPM @ 50 Hz) fan motor shall be mounted on an adjustable base, and equipped with an adjustable motor pulley. A Liebert Lee- Temp head pressure control system shall be field piped to the unit. Electrical controls shall be in a rain-tight enclosure.

The system shall be designed for _____ °F (°C) ambient. The air-cooled condenser shall have a _____ Volt, 3 phase, _____ Hz power supply.

### Water or Glycol-Cooled Self-Contained Systems

#### Indoor Unit Condenser

The water/glycol system shall be equipped with a coaxial condenser having a total pressure drop of _____ ft. of water (kPa) and a flow rate of _____ GPM (l/s) with _____ °F (°C) entering water/glycol temperature.

Two-way Water Regulating Valve with Bypass (Standard)

The condenser circuit shall be pre-piped with a headpressure actuated two-way regulating valve with bypass.

Three-Way Water Regulating Valve (Optional)

The condenser circuit shall be pre-piped with a head pressure actuated three-way regulating valve.

Design Pressure

The condenser water/glycol circuit shall be designed for a pressure of [(150 PSI (1034 kPa)) (350 PSI (2413 kPa))].

Crankcase Heater (Optional)

A crankcase heater is provided to prevent the migration of refrigerant to the compressor during off cycles.

Hot Gas Reheat (Optional)

The complete hot gas reheat system shall include a copper tube, aluminum fin coil, three-way solenoid valve, and refrigerant check valve. The capacity of the coil shall be _____ BTU/HR (kW).

70/30 Cu-Ni Econ-O-Coil

This coil replaces the standard copper tube coil to provide improved resistance to corrosion.

This option must be specified whenever a GLYCOOL or Dual Cooling Source system is applied to a cooling tower loop or other open water system.

#### Outdoor Unit

Propeller Fan Drycooler (Standard)

The Liebert manufactured drycooler shall be the low profile, slow speed, direct drive propeller fan type. The drycooler shall be constructed of aluminum and contain a copper tube aluminum fin coil with an integral electric control panel. The drycooler shall be designed for _____ °F (°C) ambient.

Centrifugal Fan Drycooler (Optional)

The system shall be supplied with a centrifugal fan drycooler (LCD). The drycooler shall be constructed of galvanized steel with a copper tube, aluminum fin coil. The heavy duty fan shall be the centrifugal type, double width, double inlet. The 1750 RPM (1450 RPM @ 50 Hz) fan motor shall be mounted on an adjustable base, and equipped with an adjustable motor pulley. A three-way control valve and thermostat shall maintain the desired fluid temperature. Electrical controls shall be in a rain-tight enclosure. The system shall be designed for _____ °F (°C) ambient. The drycooler shall have a _____ Volt, 3 phase, _____ Hz power supply.

Single Glycol Pump Package (Standard)

This system shall be provided with a centrifugal pump mounted in a weatherproof and vented enclosure. The pump shall be rated for _____ GPM (l/s) at _____ ft. of head (kPa), and operate on _____ Volt, 3 phase, _____ Hz.

Dual Glycol Pump Package (Optional)

The dual pump package shall include pumps, enclosure, and field mounted flow switch. The pumps shall be wired to the drycooler control box which includes a lead/lag switch for the pumps. The standby pump shall automatically start upon failure of the lead pump. Each pump shall be rated _____ for GPM (l/s) at _____ feet of head (kPa).

### GLYCOOL Self-Contained Systems

Econ-O-Coil

The Econ-O-Coil shall be constructed of copper tubes and aluminum fins and be located upstream of the evaporator coil. The Econ-O-Coil shall be designed for closed-loop applications using properly treated glycol solutions. Applications using a cooling tower loop or other open water system must specify a 70/30 Cu-Ni Econ-O-Coil for improved corrosion resistance. The coil shall be rated at _____ BTU/HR (kW) sensible cooling capacity with a 45°F (7.2°C) entering glycol solution temperature. The GLYCOOL coil shall require _____ GPM (l/s) and the total unit pressure drop shall not exceed _____ feet of water (kPa) when in the free cooling mode.

Three-way GLYCOOL Valve

The Econ-O-Coil coil shall be equipped with a fully proportional three-way control valve. This motorized control valve shall control the amount of flow to the Econ-O-Coil and maintain constant temperature and relative humidity.

Glycol Condenser

The glycol system shall be equipped with a coaxial condenser having a total pressure drop of _____ feet of water (kPa) and a flow rate of _____ GPM (l/s), with _____ °F (°C) entering 40% ethylene glycol temperature.

Three-way Water Regulating Valve

The condenser circuit shall be pre-piped with a head pressure actuated three-way water regulating valve.

Design Pressure

The Econ-O-Coil/condenser circuit shall be designed for a pressure of [(150 PSI (1034 kPa)) (300 PSI (2069 kPa))].

Comparator Circuit

The system shall be equipped with a microprocessorcontrolled comparator sensor that permits free-cooling operation whenever entering glycol temperature is below return-air temperature.

Propeller Fan Drycooler (Standard)

The Liebert manufactured drycooler shall be the low profile, slow speed, direct drive propeller fan type. The drycooler shall be constructed of aluminum and contain a copper tube aluminum fin coil with an integral electric control panel. The drycooler shall be designed for _____ °F (°C) ambient.

Centrifugal Fan Drycooler (Optional)

The system shall be supplied with a centrifugal fan drycooler (LCD). The drycooler shall be constructed of galvanized steel with a copper tube, aluminum fin coil. The heavy duty fan shall be the centrifugal type, double width, double inlet. The 1750 RPM (1450 RPM @ 50 Hz) fan motor shall be mounted on an adjustable base, and equipped with an adjustable motor pulley. A three-way control valve and thermostat shall maintain the desired fluid temperature. Electrical controls shall be in a rain tight enclosure. The system shall be designed for _____ °F (°C) ambient. The drycooler shall have a _____ Volt, 3 phase, _____ Hz power supply.

Single Glycol Pump Package (Standard)

This system shall be provided with a centrifugal pump mounted in a weatherproof and vented enclosure. The pump shall be rated for _____ GPM (l/s) at _____ ft. of head (kPa), and operate on _____ Volt, 3 phase, _____ Hz.

Dual Glycol Pump Package (Optional)

The dual pump package shall include pumps, enclosure, and field mounted flow switch. The pumps shall be wired to the drycooler control box which includes a lead/lag switch for the pumps. The standby pump shall automatically start upon failure of the lead pump. Each pump shall be rated for _____ GPM (l/s) at _____ feet of head (kPa).

## Direct Expansion Split Systems

Direct Expansion Coil

The evaporator coil shall have _____ sq.ft. (sq. m) face area, _____ rows deep. It shall be configured as (A) (V) frame and be constructed of copper tubes and aluminum fins and have a maximum face velocity of _____ ft. per minute (m/s) at _____ CFM (CMH). The coil shall be provided with a stainless steel drain pan.

Refrigeration System

The refrigeration system shall consist of a rugged scroll compressor, pressure safety switches, externally equalized expansion valve, filter dryer, and a refrigerant sight glass and moisture indicator.

Centrifugal Fan Condensing Unit

The condenser coil shall be constructed of copper tubes and aluminum fins. The condensing unit shall be factory assembled, charged with refrigerant and sealed.

Components shall include scroll compressor, high-pressure switch, Liebert Lee-Temp refrigerant receiver, head pressure control valve, and liquid line solenoid valve.

The condensing unit shall be designed for 95°F (35°C) ambient and be capable of operation to -20°F (-29°C) ambient.

A hot gas bypass circuit shall be provided to reduce compressor cycling and improve operation under low load conditions.

The condenser fan shall be designed for _____ CFM (CMH) at _____ inches (mm) external static pressure.

(Optional) Disconnect

Factory installed non-fused disconnect switch allows unit to be turned off for maintenance.

5-Ton Models

The fan/motor assembly shall be belt drive. Condensing unit must be hard piped with the evaporator. Sweat adapters are shipped loose with all evaporators for use on the 5 ton condensing units.

#### Propeller Fan Condensing Unit

The condenser coil shall be constructed of copper tubes and aluminum fins with a direct drive propeller type fan and shall include a scroll compressor, high pressure switch, Liebert Lee-Temp receiver, head pressure control valve, and liquid line solenoid valve. All components shall be factory assembled, charged with refrigerant and sealed. No brazing, dehydration, or charging shall be required. Condensing unit shall be designed for 95°F (35°C) ambient and be capable of operation to -30°F (-34.4°C).

A hot gas bypass circuit shall be provided to reduce compressor cycling and improve operation under low load conditions.

(Optional) Quiet-Line Models

The condensing unit shall be designed to operate at a sound level less then 58 dBa.

(Optional) High Ambient Models

The outdoor condensing unit shall be designed for design ambient operation of 105°F (40.6°C).

5-Ton Models

Condensing unit must be hard piped with the evaporator. Sweat adapters are shipped loose with all evaporators for use on the 5 ton condensing units.

### Water or Glycol-Cooled Split Systems

Water or Glycol-Cooled Condensing Unit

The water/glycol condensing unit shall be equipped with a coaxial condenser having a total system pressure drop of _____ ft. of water (kPa) and a flow rate of _____ GPM (l/s) with _____ °F (°C) entering water/glycol temperature.

Components shall include scroll compressor and high-pressure switch. The condensing unit shall be factory charged with R-22 refrigerant.

The condenser circuit shall be pre-piped with a [(2-way) (three-way)] regulating valve which is head-pressure actuated.

The condenser water/glycol circuit shall be designed for a static operating pressure of [(150 PSI (1034 kPa)) (350 PSI (2413 kPa))].

A hot gas bypass circuit shall be provided to reduce compressor cycling and improve operation under low load conditions.

A 70/30 Cu-Ni Econ-O-Coil must be specified whenever a GLYCOOL or Dual Cooling Source system is applied to a cooling tower loop or other open water system.

(Optional) Disconnect

Factory installed non-fused disconnect switch allows unit to be turned off for maintenance.

5-Ton Models

Condensing unit must be hard piped with the evaporator. Sweat adapters are shipped loose with all evaporators for use on the 5 ton condensing units.

Propeller Fan Drycooler (Standard)

The Liebert manufactured drycooler shall be the low profile, slow speed, direct drive propeller fan type. The drycooler shall be constructed of aluminum and contain a copper tube aluminum fin coil with an integral electric control panel. The drycooler shall be designed for _____ °F (°C) ambient.

Centrifugal Fan Drycooler (Optional)

The system shall be supplied with a centrifugal fan drycooler (LCD). The drycooler shall be constructed of galvanized steel with a copper tube, aluminum fin coil. The heavy duty fan shall be the centrifugal type, double width, double inlet. The 1750 RPM (1450 RPM @ 50 Hz) fan motor shall be mounted on an adjustable base, and equipped with an adjustable motor pulley. A three-way control valve and thermostat shall maintain the desired fluid temperature. Electrical controls shall be in a rain tight enclosure. The system shall be designed for _____ °F (°C) ambient. The drycooler shall have a _____ Volt, 3 phase, _____ Hz power supply.

Single Glycol Pump Package (Standard)

This system shall be provided with a centrifugal pump mounted in a weatherproof and vented enclosure. The pump shall be rated for GPM (l/s) at _____ ft. of head (kPa), and operate on _____ Volt, 3 phase, _____ Hz.

Dual Glycol Pump Package (Optional)

The dual pump package shall include pumps, enclosure, and field mounted flow switch. The pumps shall be wired to the drycooler control box which includes a lead/lag switch for the pumps. The standby pump shall automatically start upon failure of the lead pump. Each pump shall be rated for _____ GPM (l/s) at _____ feet of head (kPa).

## Chilled Water Self-Contained Systems Chilled Water Coil

The cooling coil shall have a minimum of _____ sq. ft. (sq. m) face area, _____ rows deep. The coil shall be controlled by a modulating control valve. The chilled water coil shall be designed for closed-loop applications using properly maintained water. It shall be configured as a V-frame and be constructed of copper tubes and aluminum fins and have a maximum face velocity of _____ ft. per minute (m/s) at _____ CFM (CMH). The water circuit shall be designed to distribute water into the entire coil face area. The coil shall be supplied with _____ °F (°C) entering water temperature, with a _____ °F (°C) temperature rise. The coil shall be supplied with _____ GPM (m/s) of chilled water and the pressure drop shall not exceed _____ PSI (kPa). The coil assembly shall be mounted in a stainless steel condensate drain pan.

Three-way Chilled Water Valve (Standard)

The water circuit shall include a three-way modulating valve. The microprocessor control shall position the valve in response to room conditions. Cooling capacity will be controlled by bypassing chilled water around the coil.

Two-way Chilled Water Valve (Optional)

The water circuit shall include a two-way modulating valve. The microprocessor control shall position the valve in response to room conditions. The minimum close-off pressure of the valve/actuator assembly shall be _____ PSI (kPa).

Design Pressure

The chilled water circuit shall be designed for a pressure of [(150 PSI (1034 kPa)) (400 PSI (2758 kPa))].

Flow Switch (Optional)

The flow switch shall activate the alarm system should the chilled water supply be interrupted. The switch shall be factory mounted and wired.

## Comprehensive Monitoring Solutions

(For detailed Guide Specifications on these products, refer to information posted at www.liebert.com)

- Liebert SiteScan Web System

- Liebert SiteLink Module

- Liebert Nform

- Liebert IntelliSlot Web/485 Card With Adapter and Liebert IntelliSlot 485 Card With Adapter

- Environmental Discrete Outputs Card (ENV-DO)

- Remote Contact Monitor

- RCM4

- Autochangeover Controllers

- AC3

- RAC2-8

- Universal Monitor

- Leak Detection

- Direct Read Module

- Zone Sensor

- Spot Sensor

# Execution

## Installation of Environmental Control Units

### General

Install environmental control units in accordance with manufacturer’s installation instructions. Install units plumb and level, firmly anchored in locations indicated, and maintain manufacturer’s recommended clearances.

### Electrical Wiring

Install and connect electrical devices furnished by manufacturer but not specified to be factory mounted. Furnish copy of manufacturer’s electrical connection diagram submittal to electrical contractor.

### Piping Connections

Install and connect devices furnished by manufacturer but not specified to be factory mounted. Furnish copy of manufacturer’s piping connection diagram submittal to piping contractor.

### Supply and Drain Water Piping

Connect water supply and drains to air conditioning unit. Provide pitch and trap as manufacturer’s instructions and local codes require.

## Field Quality Control

Start up environmental control units in accordance with manufacturer’s start up instructions. Test controls and demonstrate compliance with requirements.

NOTE: These Guide Specifications comply with the format outlined by the Construction Specifications Institute per CSI MP-2-1 and CSI MP-2-2. In correspondence, reference Liebert document SL-11955a_REV0_07-08.